Machine Protection
T N Todd
February 2016

---
Typical Machine Protection issues
- Plant safety and human safety
- Single parameter limits
- Parameter-combination limits
- Various component temperatures
  - Coils
  - Vacuum vessel
  - In-vessel components
- Plasma impacts
- Positive vacuum vessel pressure
  - Water leaks creating steam
  - Hydrogen deflagration (e.g. due to cryopump regeneration)
- Laser pulse energy (window damage)
- Specific event risk assessments and mitigation strategies
- Most adverse events relate to stresses, so fatigue limits apply

---
What is “safety”?
Human safety is most important but next comes safety of the plant, i.e. stopping the machine from destroying itself - “Machine Protection”:
- single parameter operational limits
- operational limits of parameter combinations
- impacts of the plasma on the machine
- fault conditions
- need for benign plasma termination procedures

---
Single parameter limits
- Toroidal field coil current
- Ohmic Heating solenoid current
- Various component temperatures
  - Coils
  - Vacuum vessel
  - Plasma facing components
- Positive vacuum vessel pressure
  - Water leaks creating steam
  - Hydrogen deflagration (e.g. due to cryopump regeneration)
- Laser pulse energy (window damage)
- Most relate to stresses, so fatigue limits apply

---
Parameter combination limits
- Crossed magnetic fields (with no electrical faults)
  - Solenoid and toroidal field
  - Vertical field and toroidal field
  - Divertor field and toroidal field
  - Resonant magnetic perturbation fields and plasma eguilibrium fields
  - Adjacent solenoidal coils with opposite current directions
- Crossed magnetic fields (due to electrical faults)
  - Toroidal field coil ejection force if one coil shorts
  - Adjacent solenoidal coils if one coil shorts
- Complex operational effects, e.g.:
  - Halo currents due to Vertical Displacement Events
  - Disruption mitigation gas causing break-down in neutral beam duct or RF antennae
  - ICRH VSWR antinode arcs puncturing vacuum bellows
  - ECRH & ICRH forbidden resonance locations (e.g. windows)

---
Component temperatures
- Coils
  - If Cu or Al, really only water temperature and I2t matters
  - If superconducting:
    - Cable and strand motion (friction)
    - Nuclear heating
    - Eddy current heating
- Coil feeders and bus-bars (especially at joints)
- Power supply components
  - Transformers, inductors...
  - Rectifiers
  - Thyristors, IGBTs...
Copper on copper:
Joint resistance (μΩ)
= y-axis ÷ contact area (mm2)
http://www.leonardo-energy.org/sites/leonardo-energy/files/documents-and-links/jointing.pdf
Section 6.0 - Jointing of Copper Busbars, David Chapman

---
Component temperatures
- Plasma facing components, due to plasma load
  - Divertor tiles
  - Limiters (especially during ramp-up and ramp-down)
- Vessel & in-vessel components due to plasma heating systems
  - Unabsorbed RF e.g. ECRH, LHH and ICRH
  - Neutral beam shine-through
ITER heating beam at minimum permitted plasma density (modelled on an orthogonal plane)
But if the plasma density was zero...
(here modelled on the far wall facets)

---
Plasma impacts
- Plasma facing components as described above
- Disruption effects
  - Eddy currents
  - Halo currents
  - Voltages induced in coils
  - Photon flash in thermal quench (or DMS)
  - Runaway electrons (penetration depth very short for W)
Changing poloidal fields create eddy currents; e.g. JET ITER-Like Wall, modelled in ANSYS:

---
Vertical Displacement Events and
Halo Currents
In a VDE, the plasma moves vertically until edge q falls significantly below ~2, and then disrupts (by 2,1 kink or TM).
Strauss, H et al, Tokamak rotation and halo current caused by disruptions, PPPL talk, 2013

---
Plasma impacts – Runaway Electrons
Fast electron “Continuous Slowing Down Approximation” range in a solid (cm = g/cm2 ÷ g/cm3)
http://physics.nist.gov/PhysRefData/Star/Text/ESTAR.html
, 19.25g/cm3
, 1.85 g/cm3
Tokamak runaway electrons are typically ~5MeV - 80MeV

---
Plasma impacts – Runaway Electrons
Fast electron “Continuous Slowing Down Approximation” range in a solid (cm = g/cm2 ÷ g/cm3)
, 2.0 g/cm3
, 19.25g/cm3

---
Risk assessment: event probability versus impact
(Challenge) frequency: ► / Including provision for the rarity of certain types of experiment	Low / Less than once in 15 calendar years / or <1/50000 per pulse	Medium / Between once in 15 calendar years and once in 10 operational weeks / or >1/50000 and <1/1000 per pulse	High or Continuous / Greater than once in 10 operational weeks / or >1/1000 per pulse
Unmitigated hazard: ▼ / - the hazard to the machine in the absence of protection, be it interlocks, operating instructions or temporary over-rides / - cumulative where appropriate to the nature of the damage and the time interval concerned
Low / Incomplete additional heating capability* for a period >1/2 session and <1 week / or loss of >1 week and < 1 year of a specific type of machine operation / or >0.01% and <0.5% permanent reduction in machine plasma performance / - below these ranges the impact is considered ‘negligible’	Protection Category: / Not applicable	Protection Category: / C	Protection Category: / B
Medium / Incomplete additional heating capability* for a period >1 week and < 1 year / or loss of >1 year of a specific type of machine operation, but not irrecoverable / or >0.5% and <20% permanent reduction in machine plasma performance	Protection Category: / C	Protection Category: / B	Protection Category: / A
High or Extreme / Incomplete additional heating capability* for a period >1 year / or irrecoverable loss of a specific type of machine operation / or >20% permanent reduction in machine plasma performance / - Note that categories in this row include irrecoverable loss of the machine (i.e. repair costs exceed value)	Protection Category: / B	Protection Category: / A	Protection Category: / A

---
Machine Protection Panel or similar
  A special committee (or else general design reviews) consider the tokamak and all the plant, assessing:
    - Failure modes affecting only the failed system
    - Failure modes impacting other systems
    - Normal operational modes adversely affecting other systems
    - The Protection Category (i.e. probability and impact)
    - The reliability required (related to Protection Category)
    - The number and types of interlock logic, e.g.(in decreasing reliability):
      - Mechanical switches and relays
      - Simple digital logic
      - Programmable logic controllers
      - Field-programmable gate arrays
      - Microprocessors
      - Human procedures
    - Hierarchy of trips (e.g. plasma control, power supply self-limit, voltage-off, open AC breakers, fire crowbar)

---
Optimisation of plasma terminations
Different emerging problems may require different plasma control responses or termination procedures...
Example aspects of JET ITER-Like Wall protection system development

---
Conclusions
- Machine protection is a deeply complex subject!
  - Machine Protection discussions can reveal new human safety issues - must involve Safety Group
  - Identify hazardous effects and their causal events
  - Categorise the events for impact and frequency
  - Develop a policy for interlock types to be used, of varying integrity and redundancy (and cost)
  - Agree a hierarchy of trip levels e.g. related to interlock type
  - Set up appropriate benign plasma termination scenarios
  - Review all machine protection systems periodically...
  - ...and whenever a plant modification is made